## Field Builder
Description | NXTag | dataType | Units
Tubing Pressure | REG_9.0.1_FLOAT | FLOAT | PSI

## Totalflow Reg Builder
App | A | B | Type | Final
9 | 0 | 0 | FLOAT | REG_9.0.0_FLOAT | Valid reg types:
FLOAT
UINT8
STR
INT16

## Floboss Reg Builder
T | L | P | Type | Final
9 | 0 | 0 | FL | PARAM_9.0.0_FL | Valid reg types:
FL
UINT8
[5 empty] | AC10 | 10 char string
[5 empty] | AC30 | 30 char string

## Modbus Reg Builder
Type | Reg Num | DataType | Final
4 | 256 | FLOAT | REG_40256_FLOAT | Valid reg types: | Prefix
|  |  |  | BOOL | 0 | Coil Registers (on off) read/write
|  |  |  | INT16 | 1 | Contact Registers (on off) read only
|  |  |  | FLOAT | 3 | Input Registers read only
|  |  |  | FLOAT-SW | 4 | Holding Registers read/write
FLOAT-SB
FLOAT-S
FLOAT-SW_FULL32
TIMER

## Ferg Beau Builder
Struct ID | Offset | DataType | Final
1028 | 2 | FLOAT | STRUCT_1028:2:FLOAT | Valid reg types: | equivalent
|  |  |  | UINT8 | ui1
|  |  |  | UINT16 | ui2
|  |  |  | UINT32 | ui4
|  |  |  | FLOAT | r4
|  |  |  | INT32 | i4

## GE SRTP Builder
Memory Area | Position (starts at 1) | DataType | Final
R | 1 | UINT16 | REG_R1_UINT16 | Memory Areas | Description | Datatypes possible
|  |  |  | I | Discrete Inputs | BOOL
|  |  |  | Q | Discrete Outputs | BOOL
|  |  |  | M | Discrete Internals | BOOL
|  |  |  | T | Discrete Temporaries | BOOL
|  |  |  | SA | SA Discrete | BOOL
|  |  |  | SB | SB Discrete | BOOL
|  |  |  | SC | SC Discrete | BOOL
|  |  |  | S | S Discrete | BOOL
|  |  |  | G | Genius Global Data | BOOL
|  |  |  | AI | Analog Inputs | UINT16,INT16
|  |  |  | AQ | Analog Outputs | UINT16,INT16
|  |  |  | R | Registers | UINT16,INT16,FLOAT,UINT32,INT32
Note: FLOATS and 32 bit INTS require two registers, eg REG_R1_FLOAT spans both the R1 and R2 register space

## Siemens Builder
Memory Area | Database (Only applicable if memory area is DB) | Address (starts at 0) | Bit position (0-7) | DataType | Final
M |  | 132 |  | FLOAT | REG_M132_FLOAT | Memory Areas | Description | Datatypes possible | Datatypes
DB | 1 | 41 | 0 | FLOAT | REG_DB1.41.0_FLOAT | I | Discrete Inputs | BOOL | UINT16,
Q |  | 1 | 3 | BOOL | REG_Q1.3_BOOL | Q | Discrete Outputs | BOOL | INT16,
[6 empty] | M | Memory | Any | UINT32,
[6 empty] | DB | Database | Any | INT32,
[6 empty] | C | Counters | Any | FLOAT,
[6 empty] | TM | Timers | Any | BOOL,
UINT8,
INT8
Note: Address is byte addressing, so REG_M0_FLOAT and REG_M4_FLOAT would be neighbor floats
Note: Bit position is required if reading from DB
Note: VD = DB1